SECTION 26 09 00

POWER CONTROLS

Display hidden notes to specifier. (Don't know how? Click Here) 
 Copyright 2023 -  2024 ARCAT, Inc. - All rights reserved

PART 1    GENERAL
1.1	SECTION INCLUDES
A.	Power Controls.
1.	Power control enclosures (Sensor, Sensor IQ, DRd, ERP, ERPA, ERP-FT).
2.	Distributed power controllers (Foundry Zone Controllers, Foundry Mini Panels, Foundry F-Drive, ColorSource Relay).
3.	Circuit and data distribution (ColorSource Raceway, 9900-series connector strips, boxes, floor pockets, and wall plates).
4.	Company Switches (PowerSafe).
5.	Emergency Lighting Controls (Bypass: ALCR, DEBC, EBDK, MPLD2. Transfer: SC1008, ELTS2).
1.2	RELATED SECTIONS
A.	Section 26 27 16 - Electrical Cabinets and Enclosures.
B.	Section 26 09 43 - Network Lighting Controls.
C.	Section 41 67 19 - Plant Safety Equipment. Building integrator shall provide integration of the lighting control system with Building Automation Systems.
1.3	SUBMITTALS
A.	Submit under provisions of Section 01 30 00.
B.	Product Data:
1.	Manufacturer's data sheets on each product to be used.
2.	Preparation instructions and recommendations.
3.	Storage and handling requirements and recommendations.
4.	Typical installation methods.
C.	Shop Drawings: Include details of materials, construction, and finish. Include relationship with adjacent construction. 
1.4	QUALITY ASSURANCE
A.	Manufacturer Qualifications: Company specializing in manufacturing products specified in this section with a minimum five years documented experience.
B.	Installer Qualifications: Company specializing in performing Work of this section with minimum two years documented experience with projects of similar scope and complexity.
C.	Source Limitations: Provide each type of product from a single manufacturing source to ensure uniformity.
1.5	PRE-INSTALLATION CONFERENCE
A.	Convene a conference approximately two weeks before scheduled commencement of the Work. Attendees shall include Architect, Contractor and trades involved. Agenda shall include schedule, responsibilities, critical path items and approvals.
1.6	DELIVERY, STORAGE, AND HANDLING
A.	Store and handle in strict compliance with manufacturer's written instructions and recommendations.
B.	Protect from damage due to weather, excessive temperature, and construction operations.
1.7	PROJECT CONDITIONS
A.	Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's recommended limits.
1.8	WARRANTY
A.	Manufacturer's standard limited warranty unless indicated otherwise.
PART 2    PRODUCTS
2.1	MANUFACTURERS
A.	Acceptable Manufacturer: ETC, Inc., which is located at:<BR />3031 Pleasant View Rd., P. O. Box 620979<BR />Middleton, WI 53562-0979<BR />Tel: 608-831-4116<BR />Fax: 608-836-1736<BR />Email: request info (mail@etcconnect.com);Web: https://www.etcconnect.com 
B.	Substitutions: Not permitted.
C.	Requests for substitutions will be considered in accordance with provisions of Section 01 60 00.
2.2	POWER CONTROL ENCLOSURES
A.	Product: Sensor3 Installation Enclosures (SR3) by ETC Inc. Power control system with high-density, professional features and exceptional reliability for lighting applications requiring power control.
1.	SR3-6 Enclosure: 6 modules, 12 circuits maximum.
2.	SR3-12 Enclosure: 12 modules, 24 circuits maximum.
3.	SR3-24 Enclosure: 24 modules, 48 circuits maximum.
4.	SR3-48 Enclosure: 48 modules, 96 circuits maximum.
5.	Mechanical:
a.	Construction: 16 ga steel.
b.	Finish: Fine-textured, scratch-resistant epoxy paint.
c.	Top and Bottom Conduit: Access through removable panels (SR3-48) or knockouts (SR3-6, SR3-12, and SR3-24).
d.	Keyed module slots prevent insertion of incompatible module types.
e.	Front access to all wiring and terminations.
f.	Full height locking door.
g.	Electrostatic air filter easily removed from door for periodic cleaning.
h.	High-efficiency cooling system with reporting.
i.	High-visibility LED status beacon.
6.	Electrical:
a.	SR3 Enclosures Accept the Following Feeds:
1)	Power:  Three-phase 120 / 208 VAC.
2)	Power:  Single-phase 120 / 240 VAC.
b.	Line Feed Frequencies: 47 to 63 Hz.
c.	Line Feed Voltage Range: 91 to 139 VAC. Max main transformer tap recommended is 135 V to allow for line fluctuation.
d.	Short Circuit Current Rating: 100,000 Amps RMS symmetrical.
7.	Thermals:
a.	32 to 104 degrees F. Electrical Room HVAC Systems: Must maintain the specified ambient temperature at all times.
b.	Relative Humidity: 10 to 90 percent non-condensing.
8.	Control: CEM3 Power Control Processor.
a.	Construction:
1)	Body: Formed steel. 
2)	Face Panel: Diecast. 
3)	Finish: textured epoxy paint.
b.	Slide-In Module: Toolless installation and removal. Spring-loaded release.
c.	Airflow Sensor: Ensures adequate airflow.
d.	Two configurable DMX512 inputs (rear, 2500 V opto-isolated).
e.	Two Ethernet ports:
1)	Front: for direct service connection.
2)	Rear: for operation on lighting control network.
f.	Graphical LCD: Eight line by 20 character for system configuration, live control, and status display.
g.	Number Pad: For quick access to dimmers.
h.	Shortcut Buttons: For Setup, about, and live control.
i.	Five Status LED Indicators: Power, Network activity, DMX-A DMX-B, and Panic.
j.	User-Programmable Presets: 64.
k.	UL 924 Listed Panic circuit with flexible configuration.
l.	Configuration Backups: Saved on USB or network.
m.	Dimmer Outputs: Regulate to maintain constant power plus or minus 1 Volt.
n.	Individual output scale voltage settings for load wiring compensation.
o.	Selectable Firing Modes: Normal, Forward Phase, Reverse Phase, Dimmer Doubled, Sinewave, and Fluorescent.
p.	Control Modes: Dimmed, Switched, Latch/lock, Always On, and Off.
q.	Selectable Dimmer Output Curves: Linear, Modified Linear, Square, Modified Square, Sensor 2.0, and five custom curves.
r.	16 bit fade resolution. Greater than 30,000 Step Resolution per 1/2 cycle.
s.	Selectable data loss behavior.
t.	Feedback:
1)	Sensor racks with CEM3 modules include basic system diagnostic reporting.
2)	Standard Rack Feedback Includes: DMX input status, rack power status, and rack temperature.
3)	Advanced Features (AF): Provides dimmer-specific status and load feedback. Requires AF dimmer rack and AF dimmer modules.
u.	Mobile Application: ThruPower System Reporter (TPSR).
1)	Mobile application shall select the circuit to configure either by scanning a QR code label applied to circuit distribution or by manual entry of circuit information.
2)	Mobile application shall allow users to set the Control Mode of the selected circuit in order to shift a ThruPower module between Dimmable and Switched mode according to the requirement of a connected load.
3)	Mobile application shall allow users to activate the circuit test function for the selected module.
4)	Power controls which do not support mobile circuit configuration from the plugin location of a supported load shall not be acceptable.
9.	Control Power Backup:
a.	RideThru Option: Seamless transfer to backup power upon loss of incoming line power.
1)	Backup power for 6 seconds during power loss.
2)	Automatically recharges from power feed.
b.	Battery Pack Option: Seamless transfer to battery power upon loss of normal power.
1)	Backup power for 30 minutes during normal power loss.
2)	Automatically recharges from power feed during normal power.
3)	Two hour recharge time from full discharge.
10.	Power Control Modules:
a.	Rated for continuous duty at 100 percent of rated load.
b.	Circuits: 1.2 kW, 1.8 kW, 2.4 kW, and 6 kW.
c.	Physical: Dual-density (two circuits per module), modular plug-in assemblies. Keyed to prevent improper insertion.
d.	Cast aluminum chassis, finished with textured epoxy paint.
e.	Circuit Breakers: Fully magnetic to eliminate nuisance tripping.
1)	Inrush Current Rating: 20x.
2)	Inrush Current Rating for PhaseAdept and ELV modules: 10x.
3)	Must Trip Rating: 125 percent, 10 to 100 seconds.
4)	Rated for 100 percent switching duty applications.
11.	Power Device: Sealed, patented assembly. Field-replaceable with screwdriver.
a.	PhaseAdept and ELV Module Power Devices: Not field replaceable.
b.	Two back-to-back SCRs per circuit (Dimmer and ThruPower modules).
c.	Per-circuit LED indicators.
d.	Mechanical held air gap relay.
e.	Integral bonded heatsink.
f.	Integral temperature sensor.
12.	Filtering: High quality toroidal filters.
13.	Sensor3 Module Series:
a.	Dimmer Series: Forward-phase dimming of tungsten, incandescent, magnetic, or cold cathode loads.
b.	Relay Series: Air-gap relays for switched power control.
c.	ThruPower Series: Configurable as a relay module for use with LED performance luminaires or as a forward-phase dimmer module for use with tungsten performance luminaires.
d.	ELV Series: Forward- or reverse-phase dimming of electronic loads.
e.	PhaseAdept Series: Forward- or reverse-phase dimming of electronic loads. Designed primarily for use with Sensor enclosures with CEM Classic or CEM+ control processors. Feature manual control options for setting dimming type and min scale.
f.	Constant Circuit Series: Non-controlled circuits with branch breakers.
14.	Standards Compliance: Listed: cULus.
15.	Quantities and configurations of Sensor3 enclosures, modules, and accessories to be supplied as shown on project drawings.
B.	Product: Sensor IQ Intelligent Breaker System by ETC Inc. Provides 120/208 V, 120/240 V, or 277/480 V mains-fed power distribution for up to 48 branch circuits. Combines high inrush rated overcurrent protection, switched power control, and power usage/breaker status reporting in a single device. Integrated DMX and Ethernet connectivity. Optional 0-10 V dimming, DALI output, contact inputs, and isolated ground bar for audio loads.
1.	IQ24 Enclosure: 24 branch breaker slots; 3-phase 120/208 V mains feed.
2.	IQ24-1 Enclosure: 24 branch breaker slots, bi-phase 120/240 V mains feed.
3.	IQ48 Enclosure: 48 branch breaker slots, 3-phase 120/208 V mains feed.
4.	IQ48-1 Enclosure: 48 branch breaker slots, bi-phase 120/240 V mains feed.
5.	IQ24-277 Enclosure: 24 branch breaker slots, 3-phase 120/208 V mains feed.
6.	IQ48-277 Enclosure: 48 branch breaker slots, 3-phase 277/480 V mains feed.
7.	Mechanical:
a.	Construction: 16-gauge steel.
b.	Finish: black, fine-textured, scratch-resistant powder coat paint.
c.	Removable outer panel includes integral locking door to limit access to electronics, breakers, and local relay overrides.
d.	Full front access with no side clearance required.
e.	Removable covers for access to Class 1 and Class 2 wiring.
f.	Complies with California building code - seismic zone four.
8.	Electrical:
a.	Mains feed power input to support 120 / 208 V three-phase four-wire or 120 / 240 V bi-phase three-wire plus ground.
b.	Max current input: 100 A at 12 circuits, 200 A at 24 circuits and 400 A at 48 circuits.
c.	Quiescent draw: <10 W with relays at steady state.
d.	Optional isolation between chassis and equipment grounding.
e.	Short-circuit current rating: 22,000 A or 65,000 A symmetrical.
f.	Overloads occurs at 50 operations of 600 percent of rated current.
g.	Feeder entry supported at top or top side.
1)	Bottom or bottom side entry supported by rotating enclosure during installation.
h.	Load wire entry supported on top, sides, or bottom.
9.	Thermals:
a.	Operating Temperature:  32 to 104 degrees F (0 to 40 degrees C).
b.	Humidity: 5 to 95 percent non-condensing.
10.	Branch breakers: 
a.	Trip mechanism: Hydraulic magnetic.
b.	Bus connection type: Stab on.
c.	Inrush-pulse tolerance: 25 times rated current for half-cycle.
d.	Load lugs accept 14-6 AWG load wiring.
e.	Integral current sensing.
f.	Integral trip sensing.
g.	Control and status provided by contact pads directly at bottom of the breaker case. No external wires or connections required for control or feedback.
h.	Visible state indication:
1)	LED On, Handle On: Output active.
2)	LED Off, Handle On: Remotely controlled off (Smart breakers only).
3)	LED Off, Handle Off: Breaker tipped/Manually off.
i.	Remote Feedback for breaker state, breaker type, current draw, and phase voltage.
11.	Smart Breakers:
a.	Integral mechanically held air gap relay.
b.	Integrated hall-effect sensors detect contact positions.
c.	Integrated solenoid for remote operation.
d.	Supports manual reset using breaker handle without power.
12.	Breaker Operational Ratings:
a.	No load-remote switching (Smart Breakers): 1,000,000 cycles.
b.	Resistive Load:  24 A (30 A branch breaker): 100,000 cycles.
c.	Resistive Load:  16 A (20 A branch breaker): 100,000 cycles.
d.	Resistive Load:  12 A (15 A branch breaker): 100,000 cycles.
e.	Electronic load: 15 A, 100,000 cycles.
f.	Handle operations: 10,000 cycles.
g.	Duty cycle of 6 full cycles (12 operations) per minute.
h.	Supports voltage isolation of 4000 V RMS.
i.	Utilizes latching state, mechanically held relays (Smart Breakers only).
13.	Breaker Models:
a.	Breakers:  120 V Smart.
1)	1-pole: 15 A, 20 A, or 30 A.
2)	2-pole: 15 A, 20 A, or 30 A.
3)	3-pole: 15 A, 20 A, or 30 A.
b.	Breakers:  120 V Non-Controlled.
1)	1-pole: 15 A, 20 A, or 30 A.
2)	2-pole: 15 A, 20 A, or 30 A.
3)	3-pole: 15 A, 20 A, or 30 A.
c.	Breakers:  277 V Smart.
1)	1-pole: 15 A, 20 A, or 30 A.
d.	Breakers:  277 V Non-Controlled.
1)	1-pole: 15 A, 20 A, or 30 A.
14.	Control: 
a.	User interface: 
1)	Graphical display with LED backlight.
2)	Button Interface With: 0 to 9 number buttons.
3)	Navigation Buttons: Up, down, back and enter.
4)	"Light bulb" test button for local preset activation, sequence and set level overrides.
5)	USB interface: For upload of setup and software updates.
b.	Control Wiring Terminations: 
1)	Control Terminals: Accept 12 AWG wire.
2)	Control Wiring Exiting Panel: Class 2.
3)	Control Terminations: Utilize removable connectors.
c.	Relay Modes: Normal (priority/HTP), latch-lock or last-action.
d.	Configurable DMX on/off threshold.
e.	Status feedback for breaker state, relay state, current drawer circuit, phase voltage and energy usage per circuit.
f.	Presets and sequences:
1)	Sixteen spaces with 64 presets per space configurable via local UI.
2)	One 16 step sequence per space.
g.	UL924 Listed emergency control bypass.
h.	Configurable Data-Loss Behavior: Play preset; Hold last look; Wait and fade.
15.	Accessories:
a.	0-10 V Dimming: 24 outputs of 0-10 V sink dimming control rated for 100 mA per output.
b.	Contact Input: 24 Dry Contact Inputs:
1)	Trigger presets and sequences, which play at priority configured for architectural sources.
2)	Directly control one or more outputs. Priority of outputs is configurable. If nothing is configured, the last action takes precedence.
c.	DALI Control: 24 control loops of broadcast DALI control.
1)	Each loop supports up to 64 ballasts.
2)	External DALI power supply required.
d.	RideThru Option: Short-term power backup of control electronics.
1)	Automatically engages when power is lost.
2)	Recharges during normal power operation.
e.	UPS Backup Kit for Load Shedding: Allows Power Control Processor to be powered via external UPS.
1)	Required for load shedding applications.
2)	Power to drive relays off when normal power is lost.
3)	UPS for Sensor IQ panel must be UL 924 Listed and rated for a minimum of 200 W peak load.
f.	Branch Circuit Fuse Kit: Aids engineers in selective coordination of emergency circuits.
16.	Standards Compliance: 
a.	Breakers: Listed to UL 489. 
b.	Enclosures: Listed to UL 67, UL 508, UL 924.
c.	Complies with ANSI DMX512-A and ANSI E1.31 streaming ACN standard.
d.	Complies with ESD immunity to IEC standard 1000-4-2.
17.	Quantities and configurations of Sensor IQ enclosures, branch circuit breakers, and accessories to be supplied as shown on project drawings.
C.	Product: Unison DRd Power Control Enclosure by ETC Inc. Power control system with high-density, professional features and exceptional reliability for lighting applications requiring power control.
1.	Enclosure Type:  DRd Enclosures.  100-120 Volt.
a.	Model DRd6-12-120. Six-module rack enclosure (12 circuits).
b.	Model DRd12-24-120. 12-module rack enclosure (24 circuits).
c.	Model DRd12-48-120. Two 12-module rack enclosures (48 circuits, requires Auxiliary Enclosure).
2.	Enclosure Type:  Auxiliary Enclosures. 100-120 Volt.
a.	Model AX12X-MCB-3-400. Auxiliary Rack with 400 A Main Breaker.
b.	Model AX12X-ML-3-400. Auxiliary Rack with Main Lugs, 3-phase.
c.	Model AX12X-ML-1-600. Auxiliary Rack with Main Lugs, 2-phase.
3.	Enclosure Type:  DRd Enclosures.  277 Volt.
a.	Model DRd6-12-277. Six-module rack enclosure (12 circuits).
b.	Model DRd12-24-277. 12-module rack enclosure (24 circuits).
c.	Model DRd12-48-277. Two 12-module rack enclosures (48 circuits, requires Auxilliary Enclosure).
4.	Enclosure Type:  Auxiliary Enclosures.  277 Volt.
a.	Model AX12X-MCB-3-400. Auxiliary Rack with 400 A Main Breaker. 
b.	Model AX12X-ML-3-400. Auxiliary Rack with Main Lugs.
5.	Mechanical:
a.	Construction: Welded 18 ga formed steel.
b.	Finish: Fine-textured, scratch-resistant epoxy paint.
c.	Mounting: Surface or floor-stand.
d.	Hinged, lockable full-height door with electrostatic air filter.
e.	Integral low-voltage fan.
f.	Modular control electronics.
6.	Electrical:
a.	Mains Feed Input:  120/208 V - 3-phase, 4-wire.
b.	Mains Feed Input:  120/240 V - bi-phase, 3-wire.
c.	Mains Feed Input:  277/480 V - 3-phase, 4-wire.
d.	Short Circuit Current Rating (SCCR):  65,000 Amp 240/277 V models.
e.	Short Circuit Current Rating (SCCR):  100,000 Amp 120/208 V models.
7.	Thermals:
a.	Ambient Room Temperature: 32 to 104 degrees F.
b.	Ambient Humidity: 10 to 90 percent non-condensing.
8.	Control Power Backup:
a.	RideThru Option: Seamless transfer to backup power upon loss of incoming line power.
1)	Backup power for 6 seconds during power loss.
2)	Automatically recharges from power feed.
b.	Battery Pack Option: Seamless transfer to battery power upon loss of normal power.
1)	Backup power for 90 minutes during normal power loss.
2)	Automatically recharges from power feed during normal power.
3)	Two hour recharge time from full discharge.
9.	Power Control modules:
a.	Rated for continuous duty at 100 percent of rated load. 
b.	Circuits: 1.8 kW and 2.4 kW.
c.	Physical: Dual-density (two circuits per module), modular plug-in assemblies. Keyed to prevent improper insertion.
d.	Cast aluminum chassis. Finish: Textured epoxy paint.
e.	Circuit Breakers: Fully magnetic to eliminate nuisance tripping.
1)	Inrush Current Rating: 20x.
2)	Inrush Current Rating PhaseAdept and ELV modules: 10x.
3)	Must-Trip Rating: 125 percent, 10 to 120 seconds.
4)	Rated for 100 percent switching duty applications.
f.	Power Device: Sealed, assembly. Field-replaceable with screwdriver.
1)	PhaseAdept and ELV modules not replaceable.
2)	Two back-to-back SCRs per circuit for D15/D20 modules.
3)	Per-circuit LED indicators.
4)	Mechanical held air gap relay.
5)	Integral bonded heatsink.
6)	Integral temperature sensor.
g.	Filtering: High quality toroidal filters.
10.	Unison DRd Module Series:
a.	Dimmer Series: forward-phase dimming of tungsten, incandescent, magnetic, or cold cathode loads.
b.	Relay Series: air-gap relays for switched power control.
c.	ELV Series: forward- or reverse-phase dimming of electronic loads.
d.	PhaseAdept Series: forward- or reverse-phase dimming of electronic loads. Designed primarily for use with legacy Unison DR enclosures. Feature manual control options for setting dimming type and min scale.
e.	Constant Circuit Series: non-controlled circuits with branch breakers.
11.	DRd Enclosure Accessories:
a.	Unison DRd Semi-Recessed Installation Kit.
1)	Meets the following guidelines for maximum protrusion when installed with 6" wall construction:
a)	ADAAG 307.2.
b)	DOJ Standards for accessible design 4.4.1.
c)	International Building Code IBC1003.3.3.
b.	Unison DRd 0-10V Option Kit. Control output for 24 circuits of 0-10 V sink dimming control.
c.	Unison DRd DALI Option Kit. Control output for 24 loops of broadcast DALI-compatible fluorescent ballasts. 
1)	Class 1 or Class 2 DALI wiring supported.
12.	Quantities and configurations of Unison DRd enclosures, modules, and accessories to be supplied as shown on project drawings.
D.	Echo Relay Panel Mains Feed (ERP) by ETC Inc. Control-oriented power center. Supports up to 24 relays or dimmers with integral branch breakers. Integrated DMX and Ethernet connectivity. Optional 0-10 V, DALI, and contact input control cards. UL 924 listed for emergency lighting control.
1.	Construction: Steel, 16 ga.
a.	Finish: Black, fine-textured, scratch-resistant powder coat. 
b.	Flush-Mount Door:  Extends 1 inch beyond all panel edges to hide wall cutout.
c.	Removable Outer Panel: Includes integral locking door to limit access to electronics, breakers, and local relay overrides.
d.	Full Front Access: No side clearance required.
e.	Removable Covers: For access to Class 1 and 2 wiring.
2.	Thermal:
a.	Operating Temperature:  32 to 104 degrees F (0 to 40 degrees C).
b.	Humidity: 10 to 90 percent, non-condensing.
3.	Electrical:
a.	Main Feed Power Input: 
1)	Power:  Single-Phase 3-Wire Plus Ground: 120/240 V.
2)	Power:  Three-Phase 4-Wire Plus Ground: 120/208 V.
b.	Separate Wiring Chambers: For Class 1 and Class 2 terminations.
c.	Max Input Current: 200 Amps.
d.	Main Circuit Breaker: 100 or 200 Amps.
e.	Branch Breaker Panel: Supports 3-phase or 1-phase sub-feed of a second panel up to 100 Amps.
f.	Short-Circuit Rating: 10,000 to 42,000 Amps symmetrical.
g.	Branch Circuit Breakers: 1, 2, or 3 pole. 10, 15, and 20 A. Rating: 80 percent.
h.	GFCI Branch Circuit Breakers: 1 or 2 pole. 120 V. 15 or 20 A.
i.	Inrush-pulse tolerance: 8 to 10.5 times rated current for half-cycle at 60 Hz.
4.	Power Control Cards:
a.	ERP 1PR:  Single-pole, 20 A relay card.
b.	ERP 2PR:  Two-pole, 20 A relay card.
c.	ERP 3PR:  Three-pole, 20 A relay card.
d.	ERP-DIM:  Single-pole, 300 W phase-adaptive dimmer card.
e.	ERP-DIM-MLV:  Single-pole, 300 W forward-phase dimmer card.
5.	Relay Ratings: 
a.	Ballast (HID): 20 A.
b.	Electronic Ballast: 16 A.
c.	Tungsten: 20 A.
d.	Motor Load: 20 A.
e.	Isolation: 4000 V RMS.
f.	State: Latching; mechanically held.
g.	Life: 100,000 cycles at full resistive load.
h.	Life: 30,000 cycles motor, inductive, or tungsten.
i.	Current-Reporting Accuracy: Plus or minus 5 percent of connected load.
6.	Dimmer Ratings:
a.	ERP-DIM:Phase-adaptive (default reverse-phase), 300 W resistive or electronic load capacity.
b.	ERP-DIM-MLV: Forward-phase, 300 W magnetic or resistive load capacity.
7.	Control: 
a.	User interface: 
1)	Graphical display with LED backlight.
2)	Button Interface With: 0 to 9 number buttons.
3)	Navigation Buttons: Up, down, back and enter.
4)	"Light bulb" test button for local preset activation, sequence and set level overrides.
5)	USB interface: For upload of setup and software updates.
b.	Control Wiring Terminations: 
1)	Control Terminals: Accept 12 AWG wire.
2)	Control Wiring Exiting Panel: Class 2.
3)	Control Terminations: Utilize removable connectors.
c.	Relay Modes: Normal (priority/HTP), latch-lock or last-action.
d.	Configurable DMX on/off threshold.
e.	Status feedback for breaker state, relay state, current drawer circuit, phase voltage and energy usage per circuit.
f.	Presets and sequences:
1)	Sixteen spaces with 64 presets per space configurable via local UI.
2)	One 16 step sequence per space.
g.	UL924 Listed emergency control bypass.
h.	Configurable Data-Loss Behavior: Play preset; Hold last look; Wait and fade.
8.	Accessories:
a.	Dimming 0-10 V: 24 outputs of 0-10 V sink dimming control rated for 100 mA per output.
b.	Contact Input: 24 dry contact inputs used to:
1)	Trigger Presets and Sequences: Play at priority configured for architectural sources.
2)	Directly Control of One or More Outputs. Priority of outputs is configurable. If no configuration, the last action takes precedence.
c.	DALI Control Loops: 24 broadcast DALI controls. Each loop supports 64 ballasts. External DALI power supply required.
d.	RideThru Option: Short-term power backup of control electronics.
1)	Automatically engages when power is lost.
2)	Recharges during normal power operation.
e.	Tamper-Proof Hardware Kit: Special screw heads prevent access to panel interior.
9.	Standards Compliance: Listed: cULus, UL508, UL67, and UL924. ANSI E1.11 DMX512-A and ANSI E1.31 streaming ACN.
10.	Quantities and configurations of Echo Relay Panel Mains Feed enclosures, power control cards, and accessories to be supplied as shown on project drawings.
E.	Echo Relay Panel 277 V (ERPA) by ETC Inc. Control-oriented power center. Supports 24 relays with integral branch breakers, power-usage reporting, and sophisticated control inputs. Integrated DMX and Ethernet connectivity. Optional 0-10 V, DALI, and contact input control cards. UL 924 listed for emergency lighting control.
1.	Construction: Steel, 16 ga. 
a.	Finish: Black, fine-textured, scratch-resistant powder coat. 
b.	Flush-Mount Door:  Extends 1 inch beyond all panel edges to hide wall cutout.
c.	Removable Outer Panel: Includes integral locking door to limit access to electronics, breakers, and local relay overrides.
d.	Full Front Access: No side clearance required.
e.	Removable Covers: For access to Class 1 and 2 wiring.
2.	Thermal:
a.	Operating Temperature:  32 to 104 degrees F (0 to 40 degrees C).
b.	Humidity: 10 to 90 percent, non-condensing.
3.	Electrical:
a.	Main Feed Power Input: 277/480 V or 240/415 V.
1)	Power:  Single-Phase 3-Wire Plus Ground: 120/240 V.
2)	Power:  Three-Phase 4-Wire Plus Ground: 120/208 V.
b.	Separate Wiring Chambers: For Class 1 and Class 2 terminations.
c.	Max Input Current: 200 Amps.
d.	Main Circuit Breaker Options: 150 and 200 Amps.
e.	Short Circuit Rating: 14,000 to 65,000 Amps symmetrical.
f.	Branch Circuit Breakers: 20 Amp. Rating: 80 percent.
g.	Inrush-Pulse Tolerance: 8 to 10.5 times rated current for half-cycle at 60 Hz.
4.	Power Control Card:  ERP 1PR - single-pole, 20 A relay card.
5.	Relay Ratings: 
a.	Ballast (HID): 20 A.
b.	Electronic Ballast: 16 A.
c.	Tungsten: 20 A.
d.	Motor Load: 14 A.
e.	Isolation: 4000 V RMS.
f.	State: Latching; mechanically held.
g.	Life: 100,000 cycles at full resistive load.
h.	Life: 30,000 cycles motor, inductive, or tungsten.
i.	Current-Reporting Accuracy: Plus or minus 5 percent of connected load.
6.	Control: 
a.	User interface: 
1)	Graphical display with LED backlight.
2)	Button Interface With: 0 to 9 number buttons.
3)	Navigation Buttons: Up, down, back and enter.
4)	"Light bulb" test button for local preset activation, sequence and set level overrides.
5)	USB interface: For upload of setup and software updates.
b.	Control Wiring Terminations: Accessible via flip down door.
1)	Control Terminals: Accept 12 AWG wire.
2)	Control Wiring Exiting Panel: Class 2.
3)	Control Terminations: Utilize removable connectors.
c.	Relay Modes: Normal (priority/HTP), latch-lock or last-action.
d.	Configurable DMX on/off threshold.
e.	Status feedback for breaker state, relay state, current drawer circuit, phase voltage and energy usage per circuit.
f.	Presets and sequences:
1)	Sixteen spaces with 64 presets per space configurable via local UI.
2)	One 16 step sequence per space.
g.	UL924 Listed emergency control bypass.
h.	Configurable Data-Loss Behavior: Play preset; Hold last look; Wait and fade.
7.	Accessories:
a.	Dimming 0-10 V: 24 outputs of 0 to 10 V sink dimming control rated for 100 mA per output.
b.	Contact Input: 24 dry contact inputs used to:
1)	Trigger Presets and Sequences: Play at priority configured for architectural sources.
2)	Directly Control of One or More Outputs. Priority of outputs is configurable. If no configuration, the last action takes precedence.
c.	DALI Control Loops: 24 broadcast DALI controls. Each loop supports 64 ballasts. External DALI power supply required.
d.	RideThru Option: Short-term power backup of control electronics.
1)	Automatically engages when power is lost.
2)	Recharges during normal power operation.
e.	Tamper-Proof Hardware Kit: Special screw heads prevent access to panel interior.
8.	Standards Compliance: Listed: cULus, UL508, UL67, and UL924. ANSI E1.11 DMX512-A and ANSI E1.31 streaming ACN.
9.	Quantities and configurations of Echo Relay Panel 277V enclosures, power control cards, and accessories to be supplied as shown on project drawings.
F.	Echo Relay Panel Feedthrough (ERP-FT) by ETC Inc. 48-output branch circuit switching and power control enclosure. Integrated DMX and Ethernet connectivity. Optional 0-10 V, DALI, and contact input control cards. UL 924 listed for emergency lighting control.
1.	Mechanical: Enclosure, covers with locking doors, and internal subpanels.
a.	Construction: Steel, 16 ga.
b.	Finish: Fine-textured, scratch-resistant powder coat paint. Color: Black.
c.	Removable Conduit Panels: On top, bottom, and sides.
d.	Full Front Access: No side clearance required.
e.	Removable Covers: For access to Class 1 and 2 wiring.
f.	Locking Doors: Controlled access to manual override switch of each relay and Class 2 wiring.
g.	Low-Voltage Wiring: Physically separated from AC by a mechanical barrier.
h.	Removable Subpanels: Containing electronics and relays.
2.	Thermal:
a.	Operating Temperature:  32 to 104 degrees F (0 to 40 degrees C).
b.	Humidity: 10 to 90 percent, non-condensing.
3.	Electrical:
a.	Discrete feed per circuit supports mixed voltage in a single panel.
b.	Single panel for 48 relays, populated in any combination of single- or double-pole.
c.	Separate Wiring Chambers: For Class 1 and Class 2 terminations.
d.	Voltage barriers: Toolless install between relays. Separation of normal and emergency circuits.
4.	Relay Kits:
a.	ERP-FT-1PRK: single-pole, 120-347 V, 20 A relay kit.
b.	ERP-FT-2PRK: two-pole, 120/208 V, 20 A relay kit.
c.	ERP-FT2P480RK: two-pole, 277/480 V, 20 A relay kit.
5.	Relay Ratings:
a.	General Purpose: 20 Amp, 347 V.
b.	Ballast (HID): 20 Amp, 347 V.
c.	Tungsten: 20 Amp.
d.	Motor Loads: 0.5 HP at 120 V. 1.5 HP at 240/277 V.
e.	SCCR: 18,000 Amp at 277 V, 1 Phase. 5,000 Amp at 277 V, 2 Phase.
f.	Inrush: 2000 Amp; 1 P only.
g.	Isolation: 2,500 V RMS.
h.	State: Latching.
i.	Relays are mechanically held.
j.	Life: 60,000 operations at full load.
k.	Terminal: Accepts 14 to 10 AWG copper wire.
6.	Control: 
a.	User interface: 
1)	Graphical display with LED backlight.
2)	Button Interface With: 0 to 9 number buttons.
3)	Navigation Buttons: Up, down, back and enter.
4)	"Light bulb" test button for local preset activation, sequence and set level overrides.
5)	USB interface: For upload of setup and software updates.
b.	User interface power input: 120 to 277 V, plus or minus 15 percent, 50/60 Hz. Less than 16 Amp.
1)	Multi-Tap Transformer Terminals: Accept 12 AWG wire.
c.	Control Wiring Terminations: Accessible via flip down door.
1)	Control Terminals: Accept 12 AWG wire.
2)	Control Wiring Exiting Panel: Class 2.
3)	Control Terminations: Utilize removable connectors.
d.	Relay Modes: Normal (priority/HTP), latch-lock or last-action.
e.	Configurable DMX on/off threshold.
f.	Control configuration:
1)	Sixteen spaces with 64 presets per space configurable via local UI.
2)	One 16 step sequence per space.
3)	UL924 Listed emergency control bypass.
g.	Configurable Data-Loss Behavior: Play preset; Hold last look; Wait and fade.
7.	Accessories:
a.	Dimming 0-10 V: 24 outputs of 0 to 10 V sink dimming control rated for 100 mA per output.
b.	Contact Input: 24 dry contact inputs used to:
1)	Trigger Presets and Sequences: Play at priority configured for architectural sources.
2)	Directly Control of One or More Outputs. Priority of outputs is configurable. If no configuration, the last action takes precedence.
c.	DALI Control Loops: 24 broadcast DALI controls. Each loop supports 64 ballasts. External DALI power supply required.
d.	RideThru: Short-term power backup of control electronics.
1)	Automatically engages when power is lost.
2)	Recharges during normal power operation.
e.	Tamper-Proof Hardware Kit: Special screw heads prevent access to panel interior.
8.	Standards Compliance: Listed to the following standards: 
a.	UL508 Listed (File: E92154) and UL924 Listed (File: E242514).
b.	Complies with ANSI E1.11 DMX512-A and ANSI E1.31 streaming ACN.
9.	Quantities and configurations of Echo Relay Panel Feedthrough enclosures, relay kits, and accessories to be supplied as shown on project drawings.
2.3	DISTRIBUTED POWER CONTROLLERS
A.	Product: Unison Foundry Zone Controllers by ETC Inc. DMX controlled, single- or dual-channel power controllers. Mount to an electrical junction box.
1.	Model:  UFD - 120 VAC, 600 W phase-adaptive dimmer - ELV, fluorescent or incandescent loads only. Single-channel output.
2.	Model:  UFD-MLV - 120 VAC, 600 W forward-phase dimmer - best for MLV loads. Single channel output.
3.	Model:  UFD-277 - 277 VAC, 600 W phase-adaptive dimmer - ELV, fluorescent or incandescent loads only. Single-channel output.
4.	Model:  UFD-277-MLV - 277 VAC, 600 W forward-phase dimmer - best for MLV loads. Single-channel output.
5.	Model:  UFR2 - 120-277 VAC, fully-rated 20 A relays. Dual-channel output.
6.	Model:  UFR-LV - 120-277 VAC, fully-rated 20 A relays with 0-10 V dimming control of compatible LED and fluorescent dimming ballasts. Dual-channel output, low voltage control circuits are electrically isolated.
7.	Mechanical:
a.	Construction: Injection-molded ABS plastic. 
b.	External heat sink. 
c.	Rated ambient room temperature:  32 to 122 degrees F  (0 to 50 degrees C).
d.	Rated ambient humidity: 5 to 95 percent non-condensing.
e.	Half-inch conduit knockout mounted.
f.	Mains voltage wiring exits through knockout mount.
g.	0-10 V dimming control wiring exits through knockout mount.
h.	DMX wiring connects to side of controller.
8.	Electrical:
a.	Mains Power Input Connections:
1)	Power Input: 120 to 277 V, 50/60 Hz.
2)	Hot (black wire): 4 sq mm (12 AWG).
3)	Neutral (white wire): 2.5 sq mm (14 AWG).
4)	Ground (green/yellow wire): 4 sq mm (12 AWG). 
b.	Relay Output Connections:
1)	Normally Open (NO): 20 Amp fully rated relay.
2)	Zone 1 (red wire): 4 sq mm (12 AWG).
3)	Zone 2 (red/white wire): 4 sq mm (12 AWG).
c.	0-10 V dimming output connections: 
1)	0-10 VDC, 100mA sink per output. Fully isolated from ground to 2500 V RMS.
2)	Zone 1 (violet and gray wire pair): 1 sq mm (18 AWG).
3)	Zone 2 (violet/white and gray/white wire pair): 1 sq mm (18 AWG).
4)	Mounting plate for low-voltage wiring installed in conduit.
d.	Dimmed Output Connection (red wire): 4 sq mm (12 AWG).
e.	DMX Input Port: Optically isolated from controller electronics.
1)	Withstands fault voltages of up to 250 VAC.
2)	Integrated DMX/RDM termination.
9.	Remote Configuration: Available via RDM controllers including:
a.	ETC DMX/RDM gateway networked to a device running ETC Concert software.
b.	ETC Control Console with RDM functionality.
c.	3rd party configuration and control products.
d.	Manual Configuration: Available via local button interface with LED indicators. 
e.	Set starting DMX address on the controller.
10.	Standards Compliance: Listed: cULus. Conforms to UL 508 and UL 2043, USITT DMX512-A (ANSI E1.11), and RDM (ANSI E1.20). Rated for plenum installation. Relays suitable for plug-load control (UFR2 and UFR2-LV only).
11.	Models and quantities of Foundry Zone Controllers to be supplied as shown on project drawings.
B.	Product: Foundry Mini Panels by ETC Inc. Four or Eight zones of DMX controlled lighting with fully rated 20 Amp relays and 0-10 V control per zone. Demand Response input for energy saving integration. UL 924 emergency lighting control bypass with power loss sense.
1.	Model:  UFMP4 - Four-zone mini panel, surface mount.
2.	Model:  UFMP4-F - Four-zone mini panel, flush mount.
3.	Model:  UFMP8 - Eight-zone mini panel, surface mount.
4.	Model:  UFMP8-F - Eight-zone mini panel, flush mount.
5.	Mechanical:
a.	Construction: 16 ga cold-rolled steel.
b.	Finish: Fine-textured, black powder coat.
c.	Flush or surface mount. Rated for installation in plenum air space.
d.	Rated Ambient Room Temperature: 32 to 122 degrees F (0 to 50 degrees C).
e.	Rated Ambient Humidity: 5 to 95 percent non-condensing.
f.	Class 1 Voltage Barrier: Stops line voltage wiring access with front panel removed.
g.	Voltage Dividers: Allows separation of normal and emergency circuits in a single controller where allowed by local codes.
6.	Electrical: 
a.	Power Input: 100-277 VAC, 50/60 Hz per circuit. Support for pass thru to multiple outputs.
1)	Supports 120 VAC and 277 VAC circuits within the same panel.
b.	Single-Phase Normal Power Loss Sense Circuit Input: 100-277 VAC.
c.	Fully Rated Bi-State Latching Relay per Output: 20 Amp.
d.	0-10 VDC control rated for up to 100 mA sink per output.
1)	0- 10 V outputs are fully isolated from ground to 2500 V RMS.
e.	DMX Input Port: Optically isolated input from the Mini Panel electronics.
1)	Withstands fault voltages of up to 250 VAC.
2)	Integrated DMX/RDM termination.
f.	Rising Clamp Screw Terminal Wiring Connections for:
1)	Line-voltage relay power input, output and pass-through with support for 2.5 to 10 sq mm (14 to 8 AWG) wire.
2)	Controller power input and UL 924 Sense circuit with support for 0.5 to 4 sq mm (20 to 12 AWG) wire.
3)	Low-voltage 0- 10 V dimming output per zone with support for 0.5 to 1.5 sq mm (22 to 16 AWG) wire.
4)	Separate normal power sense feed input for UL 924 emergency lighting bypass.
5)	UL 924 emergency lighting control contact closure input with support for 0.5 to 1.5 sq mm (22 to 16 AWG) wire.
6)	Demand Response contact input with support for 0.5 to 1.5 sq mm (22 to 16 AWG) wire.
7.	Relay Ratings:
a.	Magnetic Ballast (HID): 20 Amp.
b.	Electronic Ballast: 10 Amp.
c.	Tungsten: 20 Amp.
d.	Motor at 120 VAC: (120 A Locked rotor) 20 Amp.
e.	Motor at 277 VAC: (84 A Locked rotor) 14 Amp.
f.	Relays are mechanically held.
g.	Lifespan: 100K cycles, full resistive load. 30K cycles motor, inductive or tungsten.
8.	Manual Configuration:
a.	DMX: Starting channel number of output 1. Remaining outputs automatically configured contiguously.
b.	Demand Response:
1)	Manual dial to set Demand Response level.
2)	Slide switch configuration for Demand Response inclusion per output (on/off).
3)	Contact closure input supports Normally Open (NO) operation.
c.	UL 924 Emergency lighting control bypass:
1)	Slide Switch Configuration for: UL 924 operation (NO/NC) and UL 924 inclusion per circuit (on/off).
2)	UL 924 contact closure input: Normally open (NO) or normally closed (NC) operation.
d.	Onboard LED Status Indicators: For controller power, DMX signal, Demand Response input, and UL 924 emergency lighting control.
9.	Remote Configuration: Available via RDM devices such as:
a.	ETC Control Console with RDM functionality.
b.	ETC DMX/RDM gateway networked to a device running ETC Net3 Concert software.
10.	Standards Compliance: Listed: cULus. Conforms to UL 508, UL 924, and UL 2043, USITT DMX512-A (ANSI E1.11), and RDM (ANSI E1.20). Rated for plenum installation. Suitable for plug load control.
11.	Models and quantities of Foundry Mini Panels to be supplied as shown on project drawings.
C.	Product: Foundry F-Drive R12 LED Driver, F-Drive Series by ETC Inc. Rack-mounted LED driver enclosure.
1.	Rack Mount Enclosure: Model: FDR12FD F-Drive Rack-Mount Enclosure with DMX/RDM control card. Designed to utilize 12 output cards. Rack Enclosures support use of any combination of F-Drive R12 output cards providing additional rack features.
a.	Construction: 0.063 inch 5052-H53 aluminum, free of burrs and pits. 
1)	Conforms to standard equipment rack dimensions, nominally 19 inches wide and 2U high.
2)	Two ' U' handles finished in orange on front panel for insertion and removal with compatible equipment rack.
3)	Front panel: 1 control card slot and 12 output card slots. Control card to be factory installed. Output card slots to be factory fitted with removable blank plate secured via a screw. Blank plates may be removed to install optional F-Drive R12 output cards.
4)	Rear of enclosure: House electrical connections and power switch.
5)	Exterior surfaces: Finished in P1018 Dark Gray, fine textured, scratch-resistant, powder coat paint.
6)	Powered by and depend on a separate outboard 48VDC power supply.
b.	Dimensions (HxWxD): 3.46 x 19 x 12.63 inches, without output cards.
c.	Weight: 9.22 lbs.
d.	Force Air Cooled: 2 fans mounted on left side of enclosure and passing air across internal components. Intake to be left side with exhaust vents on right side of enclosure.
1)	Fans maintain component temperature at proper operating levels while under full load, provided ambient temperature does not exceed 104 degrees F. 
e.	Designed to allow insertion and removal of control and output cards without using tools.
1)	Nylon support rails provide precise card alignment into connector blocks. 
2)	Support use of any combination of F-Drive R12 output cards to provide additional rack features. Output card options shall include the fooling item.
f.	Thermal:
1)	Ambient room temperature:  32 to 104 degrees F  (0 to 40 degrees C).
2)	Ambient humidity: 5 to 95 percent non-condensing.
2.	Output Cards:
a.	Model: FDROCCC150. Constant Current Output Card.
1)	Four channel Constant Current driver card designed to work with compatible CC LED luminaire with compatible electrical characteristics including four ArcSystem Navis 100 White luminaires.
a)	Four individually addressable outputs.
b)	Constant Current output.
c)	50 W maximum per circuit (up to card limit).
d)	150 W maximum card limit.
e)	Output provided to both RJ45 and terminal connectors.
f)	200-700 mA drive current adjustable in 50 mA increments.
b.	Model: FDROCCV150. Constant Voltage Output Card.
1)	A Four channel 24V Constant Voltage driver card specifically designed to work with any compatible CV LED luminaire with compatible electrical characteristics.
a)	Four individually addressable outputs.
b)	24 VDC Constant Voltage output.
c)	50 W maximum per circuit (up to card limit).
d)	150 W maximum card limit.
e)	Output provided to terminal connectors only.
c.	Model: FDROCFTW150. FTW Output Card.
1)	A Four channel Constant Current driver card specifically designed to work with up to four ArcSystem Navis 100 Fade-To-Warm luminaires.
a)	Four individually addressable outputs.
b)	Constant Current output.
c)	50 W maximum per circuit (up to card limit).
d)	150 W maximum card limit.
e)	Output provided to both RJ45 and terminal connectors.
f)	Fixed 450 mA drive current for use with ArcSystem Navis 100 FTW luminaire only.
d.	Model: FDROCCHC100. Chroma Output Card.
1)	A Four channel driver card specifically designed to work with up to four ArcSystem Navis 100 RGBW luminaires.
a)	Four individually addressable outputs.
b)	Provide 48 VDC and data communications to luminaire.
c)	100 W maximum card limit.
d)	Output provided to RJ45 connector only.
e)	For use with ArcSystem Navis 100 RGBW luminaire only.
e.	Model: FDROCAC150. ArcLamp Output Card.
1)	ARCLAMP-150 - A Four channel driver card specifically designed to work with up to eight ETC ArcLamp luminaires per channel.
a)	Four individually addressable outputs.
b)	Provide 24 VDC constant voltage and data communications to ArcLamp luminaire.
c)	Supports up to Eight 4.4W ETC ArcLamp luminaires per channel.
d)	150 W maximum card limit.
e)	Output provided to terminal connectors only.
f)	For use only with ETC ArcLamp luminaires.
3.	Electrical:
a.	Unit to be 48 VDC input. Rated Class 2/LVLE/SELV/LPS device.
1)	Powered via external 48 VDC power source.
2)	1500 W maximum combined unit power.
3)	Overall Power Switch: Rear of unit. Contains resettable over-current breaker.
4)	External Power Source: to be approved by ETC Inc. for use with F-Drive system. Minimum requirements.
5)	100-240 VAC input voltage range.
6)	50-60Hz input frequency range.
7)	Ability to house three output power rectifiers that have no less than 1800 W max output power per rectifier.
8)	Supports rectifier hot swap (hot plug).
9)	Active current sharing.
10)	Common DC output terminals providing facility to combine output stage power of up to 9 power rectifiers.
11)	External Power Supply:
a)	Model: FDRPS1F Power Supply Three-Bay Frame (Meanwell RKP-1U System) (Frame holds up to three (3) FDRPS1M below).
b)	Model: FDRPS1M Power Supply Module (Meanwell RCP-2000-48) Power cord connection type chosen below; one cord required for each FDRPS1M.
c)	Model: FDRPSICE15 F-Drive Rack-Mount Power Supply Power Cord 14/3 NEMA 5-15P to Locking C19 IEC Connector.
d)	Model: FDRPSICE20 F-Drive Rack-Mount Power Supply Power Cord 12/3 NEMA 5-20P to Locking C19 IEC Connector.
e)	Model: FDRPSICS16 F-Drive Rack-Mount Power Supply Power Cord 14/3 (2.5 mm2) Euro Schuko Plug to Locking C19 IEC Connector.
f)	Model: FDRPSICS16 F-Drive Rack-Mount Power Supply Power Cord 14/3 (2.5 mm2) Bare Ends (Euro) to Locking C19 IEC Connector.
4.	External Power Supply and F-Drive R12: Connected to each other via DC power harness and bussing kit. Bussing kits are available for varying numbers of power source/R12 configurations.
a.	F-Drive Rack Mount Power Supply Bussing Kit:
1)	Model: FDRPS1BK1-1. 1 Power Supply / 1 F-Drive.
2)	Model: FDRPS1BK1-2. 1 Power Supply / 2 F-Drive.
3)	Model: FDRPS1BK1-3. 1 Power Supply / 3 F-Drive. 
4)	Model: FDRPS1BK2-4. 2 Power Supply / 4 F-Drive.
5)	Model: FDRPS1BK2-5. 2 Power Supply / 5 F-Drive.
6)	Model: FDRPS1BK2-6. 2 Power Supply / 6 F-Drive.
7)	Model: FDRPS1BK3-7. 3 Power Supply / 7 F-Drive.
8)	Model: FDRPS1BK3-8. 3 Power Supply / 8 F-Drive.
9)	Model: FDRPS1BK3-9. 3 Power Supply / 9 F-Drive.
10)	Unit to have the following rear-mounted connections for DC output connectivity of load/luminaires:
a)	Twelve RJ45 connectors: May be used in conjunction with a Constant Current type output card only.
b)	Twelve 8-position removable cable headers: May be used in conjunction with a Constant Current or Constant Voltage type output card and support termination of maximum 2.0sq mm (14 AWG) conductors.
c)	Rack enclosure to be fully compliant and support use of ANSI E1.11 USITT DMX512-A.
d)	DMX input/thru and have two 3-position wire terminal headers for termination of compatible wiring such as Belden 9729 or equivalent.
e)	A dry/wet (selectable) contact closure input for purposes of proving a remote trigger to override and activate present channel outputs to 100 percent during a test or remotely triggered panic scenario.
f)	A wire-terminal header providing 48 VDC pass-through of primary DC power input for purposes of down-stream voltage presence monitoring.
5.	Control: 
a.	RDM Configuration: Compliant with Remote Device Management Standard and have the following parameters:
1)	Remote status messages including:
a)	Board overtemp.
b)	Fan error.
c)	Fixture overtemp (with compatible luminaire).
d)	Fixture overcurrent/short circuit.
2)	DMX personality (With compatible luminaire).
3)	DMX start address.
4)	Identify device.
5)	Minimum level set.
6)	Maximum level set.
7)	Fade curve selection (with compatible luminaire).
8)	Configurable DMX loss behavior.
9)	FTW Temperature Scaling (with compatible luminaire).
10)	Red shift enable/disable (with compatible luminaire).
11)	The unit shall be firmware upgradeable without the need to remove the enclosure from the rack.
6.	Standards Compliance: Listed: cULus. ANSI/UL STD.8750; UL 2108, Low Voltage Lighting Systems UL 1598. Certified to CSA STD. C22.2 No: 250.13.
a.	CE Compliant, UKCA Compliant, EAC Compliant.
7.	Models and quantities of Foundry F-Drive enclosures and output cards to be supplied as shown on project drawings.
D.	Product: Foundry F-Drive W1 / W1E, F-Drive Series by ETC Inc. Wall-mount LED luminaire power solution. Configurable constant current and constant voltage versions with option to add dual input emergency support.
1.	Model: FDW1 - F-Drive W1.
a.	Output Type: CCD - Constant Current Driver.
b.	Output Type: CVD - Constant Voltage Driver.
c.	Output Type: FTWD - Fade to Warm Driver.
d.	Output Type: CHD - Chroma Driver.
2.	Model: FDW1E - F-Drive W1 Emergency version.
a.	Output Type: CCD - Constant Current Driver.
b.	Output Type: CVD - Constant Voltage Driver.
c.	Output Type: FTWD - Fade to Warm Driver.
3.	Physical:
a.	Materials: Steel enclosure, fine-textured, scratch-resistant powder coat paint.
b.	Color: Equinox grey
c.	Mounting: Four mounting holes on the interior of the enclosure.
d.	Mounting: External mounting strips for mounting without removing front cover.
e.	Cable Cutout: Removable plate for contractor hole punching / drilling.
f.	IP Rating: IP-20 (dry location).
g.	Humidity: 5 0 95 percent non-condensing.
h.	Weight: 6.7 lbs.
4.	Thermal:
a.	Ambient operating temperature:  32 to 104 degrees F  (0 to 40 degrees C).
b.	Fan, Controllable: Convection cooled.
c.	BTUs/hour, (120 V/240 V): 581 BTU/hr.
5.	Electrical:
a.	Voltage Input: 100 - 277 VAC 50/60 Hz.
b.	Power factor: Greater than 0.9.
c.	Output connector: RJ45 and terminal connectors.
d.	Inrush: 15 A at 120 V (first half-cycle).
e.	Inrush: 27 A at 240 V (first half-cycle).
f.	Output: Constant current driver (CCD).
1)	Output: 200- 700 mA drive current adjustable via RDM.
2)	Output Wattage max per Circuit: 50 W up to card limit.
3)	Max Luminaire Load per Driver: 150 W.
4)	Output Connector: RJ45 and terminal.
5)	Max input current per W1 unit: 3.1 A.
6)	Max input wattage per W1 unit: 170 W.
g.	Output: Constant voltage driver (CVD).
1)	Output: 24 VDC.
2)	Output Wattage max per Circuit: 50 W up to card limit.
3)	Max Luminaire Load per Driver: 150 W.
4)	Output Connector: Terminal only.
5)	Max input current per W1 unit: 6.2 A.
6)	Max input wattage per W1 unit: 170 W.
h.	Output: Fade to warn driver (FTWD).
1)	Output: 450 mA drive current for ArcSystem Navis 100 FTW luminaires.
2)	Output Wattage max per Circuit: 50 W up to card limit.
3)	Max Luminaire Load per Driver: 150 W.
4)	Output Connector: RJ45 and terminal.
5)	Max input current per W1 unit: 3.1 A.
6)	Max input wattage per W1 unit: 170 W.
i.	Output:  Chroma driver (CHD).
1)	Output: 48 VDC power and data.
2)	Output Wattage max per Circuit: 22 W.
3)	Max Luminaire Load per Driver: 100 W.
4)	Output Connector: RJ45 only.
5)	Max input current per W1 unit: 1.7 A.
6)	Max input wattage per W1 unit: 170 W.
6.	Control: Protocols DMX and RDM.
a.	RDM Configuration: Yes.
b.	UI Type: None.
c.	DMX footprint 4 individually addressable channels.
d.	Local Control: No.
e.	Input method DMX-512 via terminal connections.
7.	Standards Compliance:
a.	Standard Version: cULus listed to UL 8750 and CSA C22.2 No. 250.13.
b.	Emergency Version:
1)	cULus listed to UL 8750 and CSA C22.2 No. 250.13.
2)	cULus listed to UL 924 and CSA C22.2 No. 141 Certified by Lloyd's Registry.
3)	Suitable for use in air handling systems by NEC 300.22(C)(3).
8.	Models and quantities of Foundry F-Drive drivers to be supplied as shown on project drawings.
E.	Product: Foundry B-Box by ETC Inc. An accessory that expands connection capabilities of the F-Drive LED driver system. Converts a Cat6 cable run with an RJ45 into four different single-channel outputs, for Molex, two-pin terminal, or even single-channel RJ45 cable runs. Compatible with CC and FTW output models in the F-Drive R12 and W1 product line.
1.	Model: FD-BBOX-4T. B-Box with four, two-pin terminal connectors to support constant current loads requiring 200 to 700 mA.
2.	Model: FD-BBOX-4R. B-Box with four RJ45 outputs to support a single ArcSystem Navis White or Fade to Warm luminaire per output.
3.	Model: FD-BBOX-4M. B-Box with four Molex outputs to support ArcSystem Pro One-Cell, Pro One-Cell Small, and Pro One-Cell Micro luminaires.
4.	Mechancial:
a.	Materials: Plenum rated plastic with aluminum connector plates.
b.	Color: Black.
c.	Mounting: Set freely on feet or screw to structure using mounting bracket.
d.	Mounting: Lanyard for installations requiring a secondary tether.
e.	IP rating: IP-20; dry locations only.
5.	Thermal:
a.	Ambient Operating Temperature: 32 to 104 degrees F.
b.	Humidity: 5 to 95 percent non-condensing.
6.	Electrical:
a.	Input: Four channels via RJ45 from F-Drive R12 or W1. Works with: FDROCCC150, FDROCFTW150, FDW1CCD, or FDW1FTWD.
b.	Output: Each output connection represents a single channel of luminaire control and power.
c.	Maximum cable length from F-Drive R12 to luminaire: 328 ft total, from F-Drive R12 output card or F-Drive W1 Driver to final luminaire. B-Box neither extends, nor counts against this distance.
7.	Standards Compliance: Listed: cETLus and Listed to UL 62368-1. Certified to CSA 22.2 no 62368-1. CE and UKCA Compliant.
a.	Suitable for use in air handling systems by NEC 300.22(C)(3)
b.	If used with an Emergency lighting Circuit, follow NEC Marking requirements or local jurisdiction requirements.
8.	Models and quantities of Foundry B-Box to be supplied as shown on project drawings.
F.	Product: ColorSource Relay as manufactured by ETC Inc.
1.	Model CSR-D - hardwired DMX/RDM in-and-thru with:
a.	DMX input cable, 5 ft.
b.	DMX input cable, 10 ft.
c.	DMX input cable, 15 ft.
2.	Model CSR-M - wireless City Theatrical Multiverse DMX/RDM transceiver and hardwired DMX/RDM output with:
a.	City Theatrical Multiverse ShoW Baby (Multiverse and ShoW DMX transceiver, one DMX universe).
b.	City Theatrical Multiverse Node (Multiverse transceiver, one DMX universe).
c.	City Theatrical Multiverse Transmitter (Multiverse transceiver, ten DMX universes).
3.	Power input cable to consist of:
a.	Edison plug to powerCON receptacle, 5 ft.
b.	Stage pin (2P&G/GPC) plug to powerCON receptacle, 5 ft.
c.	Twistlock (L5-20) plug to powerCON receptacle, 5ft.
d.	Bare end pigtail (plug type TBD) to powerCON receptacle, 5 ft.
4.	Physical:
a.	Construction: Molded textured black plastic; convection cooled.
b.	Power Input/Output Connections: Neutrik powerCON at 45 degrees.
c.	Hardwired DMX Connections: 5-pin XLR (required DMX terminator not included).
d.	Mounting: Pipe, yoke, or wall. Required mounting accessories not included.
e.	Environmental:  32 to 104 degrees F  (0 to 40 degrees C); 5 to 95 percent non-condensing humidity; IP20, not rated for outdoor use.
f.	Included Accessories: Power cable (CSR-D and CSR-M, see above for options), 2 dBi gain omnidirectional antenna (CSR-M only).
5.	Electrical:
a.	Voltage Range: 90-250 VAC; 47-63 Hz; supports 120 V, 120/208 V and Delta power input. Max Current: 16 A.
b.	Relay: 2-pole air gap rated for 100,000 cycles at 16 A, 250 V.
1)	Auto sequencing and zero-cross switching functions included to minimize nuisance tripping.
2)	Relays without auto sequencing and zero-cross switching shall not be accepted.
c.	Isolation: 2,500 V RMS.
d.	Quiescent power consumption: CSR-D: 0.25 W and CSR-M: 0.65 W.
6.	Control:
a.	Protocols:  DMX512A, RDM, City Theatrical ShoW DMX Neo and Multiverse.
b.	Configuration via:
1)	RDM via software such as ETC Concert or Eos.
2)	Local USB port; also used for software update.
3)	Local wireless ID selection, CSR-M only.
c.	Configurable Relay Mode:
1)	Auto Mode: Automatically switches on and off by detecting DMX/RDM signal.
2)	DMX Mode: Switches on and off based on DMX control level.
3)	RDM Mode: Switches on and off via RDM command.
4)	Relays without configurable operation modes shall not be accepted.
d.	Wired performance:
1)	Range: 500 m.
2)	Max receivers DMX: 32. RDM: 32.
e.	Wireless performance (Multiverse, ShoW DMX Neo):
1)	Band: 2.400 to 2.480 GHz.
2)	Range: 100 m indoors, 500 m line of sight; subject to conditions.
3)	Broadcast Power: 100 mW EIRP.
4)	DMX Latency: ShoW DMX Neo: 7 ms; Multiverse: 4 ms.
f.	RDM Performance: ShoW DMX Neo: DMX pause 100 ms; Multiverse: non-interfering.
7.	Regulatory and Compliance: Conforms to UL 508. Certified to CSA C22.2 No. 14. cETLus Listed. CE Compliant.
8.	Models and quantities of ColorSource Relay to be supplied as shown on project drawings.
2.4	CIRCUIT AND DATA DISTRIBUTION
A.	Product: ColorSource Raceway by ETC Inc.
1.	Mechanical:
a.	Construction:
1)	Raceway: 1.6 mm thick extruded aluminum. (HxD): 5 x 1.77 in (127 x 45 mm).
2)	Terminal box: 1.6 mm thick extruded aluminum. (HxD) 5 x 3 in. (127 x 78 mm).
3)	Connector Plates and Frames: 1/8 inch (3 mm) diecast aluminum. Each frame supports two plates.
b.	Maximum length: 72 ft (22 m) with:
1)	One terminal box (required), 1 ft (305 mm) long.
2)	Up to 71 connector frames, 1 ft (305 mm) long.
3)	Finish: Fine-textured, black powder coat paint. 
4)	Circuit Labeling: Above each connector with (15 mm) reverse silk screened lexan labels.
5)	Ship wired and folded in 6 ft (1.8 m) lengths with splicing hardware.
6)	Hanger Brackets: ASTM a5008 steel, conforming to ISO 898-1 class 8.8. Finish: Fine-textured, black powder coat paint. Required every 10 ft (3 m), min.
a)	Wall or ceiling mount.
b)	Pipe grid mount.
c)	Wire rope suspension mount, single pipe batten.
d)	Wire rope suspension mount, double pipe batten.
e)	Threaded rod or strut mount, single pipe batten.
f)	Threaded rod or strut mount, double pipe batten.
g)	Wire rope suspension mount with ETC Rigging RACA.
h)	Catwalk railing mount.
c.	WebPipe Batten: 1.9 inch O.D. extruded aluminum pipe with vertical web.
1)	Pipe Wall and Web: 3.8 mm aluminum. Finish: Black or clear hard coat anodization.
2)	Maximum Distributed Load: 150 lbs over a 10 ft span (68 kg over 3 m).
3)	Maximum Point Load: 65 lbs over a 10 ft span (29 kg over 3 m).
4)	Safety Factor: 10:1.
2.	Electrical:
a.	Connector Strips: 120- 240 VAC 50/60 Hz branch circuit power inputs with support for multiple outputs per input.
b.	Wire Entry: Terminal box with support for eight 20 A inputs utilized for:
1)	Six circuits for power distribution along length of connector strip for performance lighting.
2)	One circuit dedicated for work lights.
3)	One circuit dedicated for DMX Active Pass-thru connectors. Can also be powered from one of the six performance lighting circuit terminals.
4)	Screwless Tension Clamp Terminals: For power input accepts 20-8 AWG (0.5 to 6 sq mm) wire for lighting circuits, 20-12 AWG (0.5 to 4 sq mm) for optional work light and DMX Active Pass-thru circuits.
c.	Belden 9729, or equal, or standard Category cable DMX/RDM input.
d.	Power Output Receptacles: Available in any combination of the following on a single strip:
1)	20 Amp Edison (5-20R).
2)	20 Amp duplex Edison (5-20RD).
3)	20 Amp grounded stage pin (GPC/2P&G).
4)	20 Amp Twist-lock (L5-20R).
5)	20 Amp powerCON TRUE1.
e.	Available Data Outlets: Supports one of the following options per raceway:
1)	One chain of 5-pin XLR DMX/RDM Active Pass-thru connectors.
a)	Max of 32 RDM devices and 24 connectors.
2)	One RJ45 Ethernet port.
3)	One passive 5-pin XLR DMX output.
f.	Work light: Integrates via driver mounted in a connector plate and attaches directly to compatible hanger brackets.
1)	Beam Angle: 1,600 lumen, 3000 K CCT LED at 90 CRI, 60 degrees.
2)	Power Consumption: 25 W.
3.	Standards Compliance: cULus Listed to UL 1573 and CSA C22.2 No. 166.
4.	ColorSource Raceways to be supplied as shown on project drawings.
B.	Product: 9900 Series Connector Strip by ETC Inc. 
1.	Mechanical:
a.	Construction:
1)	Raceway: 18 ga galvanized steel.
2)	End caps and junction brackets: 14 ga galvanized steel.
3)	Covers and faceplates: 16 ga galvanized steel.
b.	Dimensions: (HxD): 6.25 x 3.3 in. (159 x 84 mm); Lengths as specified.
c.	Weight: 6 lb per ft (8.9 kg per m).
d.	Finish: Fine-textured black powder coat paint.
e.	Finish: Fine-textured powder coat. Color: ______.
f.	Circuit Labels:
1)	2 in. (50 mm); vinyl; white lettering on black; front only.
2)	Size: ___; vinyl, polycarbonate, lamicoid, or engraved; ____(color) lettering on _____ (color) background; front only or front and back.
3)	QR Code Labels: Allow users plugging in luminaires to configure ETC Sensor ThruPower modules to dimmed or switched mode via Wi-Fi connection from ThruPower System Reporter mobile app by ETC Inc.
g.	Ship wired and folded in 6 ft (1.8 m) lengths with splicing hardware.
h.	Hanger Brackets: 1.50 x 0.188 inch ASTM A36 steel with ASTM A307 grade 5 hardware. Finish: Fine-textured black powder coat paint.
1)	Wall or ceiling mount.
2)	Pipe grid mount.
3)	Wire rope suspension mount, single pipe batten.
4)	Wire rope suspension mount, double pipe batten.
5)	Threaded rod or strut mount, single pipe batten.
6)	Threaded rod or strut mount, double pipe batten.
7)	Wire rope suspension mount with ETC Rigging RACA.
8)	Catwalk railing mount.
i.	LED Indicators: Indicate presence of power at local circuits. Red in color.
1)	Mounting Location:  Lower right corner of the receptacle plate. 
2)	Mounting Location:  Center of the receptacle plate. 
3)	Mounting Location:  Bottom of connector strip below the receptacle plate. 
j.	WebPipe Batten: 1.9 inch O.D. extruded aluminum pipe with vertical web.
1)	Pipe Wall and Web: 3.8 mm aluminum. Finish: Black or clear hard coat anodization.
2)	Maximum Distributed Load: 150 lbs over a 10 ft span (68 kg over 3 m).
3)	Maximum Point Load: 65 lbs over a 10 ft span (29 kg over 3 m).
4)	Safety Factor: 10:1.
2.	Electrical:
a.	Wire Entry: At one end using feed-through terminals individually labeled with corresponding circuit numbers.
1)	Circuits, 20 Amp: Screwless tension clamp terminals listed for 20 to 8 ga wire.
2)	Circuits, 50 Amp: Compression terminals listed for 10 to 1 ga wire.
b.	Internal Wiring: Sized to circuit ampacity. Rated at 125 degrees C.
c.	Power Output Pigtails and Receptacles:
1)	Pigtails and Receptacles: Mounted on 3 in (76 mm) plates.
2)	Pigtails: Three-wire type "S" jacketed cable sized for the maximum circuit ampacity. Available in 18 in, 24 in., 36 in., or custom length. 
3)	Available in any combination of the following on a single strip:
a)	20 Amp Edison (5-20R).
b)	20 Amp duplex Edison (5-20RD).
c)	20 Amp grounded stage pin (GPC/2P&G).
d)	50 Amp grounded stage pin (GPC/2P&G).
e)	20 Amp Twist-lock (L5-20).
f)	20 Amp 208 V Twist-lock (L6-20).
g)	20 Amp powerCON TRUE1.
h)	20 Amp 16-pin multicircuit connector (Veam-Socapex compatible/VSC).
d.	Available Data Outlets: Supports the following options per connector strip:
1)	Max total of 6 data inputs, Active Pass-thru chains count as two inputs:
2)	Chain of 5-pin XLR DMX/RDM Active Pass-thru connectors.
a)	Max of 24 connectors and 32 RDM devices per chain.
3)	Passive 5-pin XLR DMX outputs (1 connector per data input; upstream optosplitter or DMX gateway required for multiple inputs).
4)	RJ45 Ethernet (sACN) ports (1 connector per data input).
5)	Integrated ETC Response 1-port Gateways (1 per data input).
6)	Integrated ETC Response 2-port Gateways (1 per data input).
3.	Standards Compliance: cULus Listed to UL 1573 and CSA C22.2 No. 166.
4.	Connector strips to be supplied as shown on project drawings.
C.	Product: Circuit and data distribution as supplied by ETC Inc. 
1.	Pigtail and outlet boxes.
2.	Gridiron junction boxes.
3.	Floor pockets and wall pockets.
4.	NEMA wall plates.
5.	Electronic control plug-in boxes (ECPB).
6.	Mechanical:
a.	Construction: Boxes constructed from 18 ga and 14 ga steel. NEMA and ECPB faceplates constructed of aluminum.
b.	Finish: Fine-textured black powder coat.
c.	Include mounting brackets and hardware.
7.	Electrical:
a.	Wire Entry: Conduit knockouts to feed-through terminals individually labeled with corresponding circuit numbers.
b.	Wire Exit: Connectorized receptacles, conduit knockouts, or cable glands.
c.	Low voltage barriers or junction boxes as required.
8.	Finish: Fine-textured black powder coat paint.
9.	Finish: Fine-textured powder coat. Color: ______.
10.	Circuit Labels:  2 in. (50 mm); vinyl; white lettering on black; front only.
11.	Circuit Labels, Custom:
a.	Size (WxH):  ___ x ___ inches (___ x ___ mm).
b.	Lettering:  Vinyl. Color:  ________. 
c.	Lettering:  Polycarbonate. Color:  ________. 
d.	Lettering:  Lamicoid. Color:  ________. 
e.	Lettering:  Engraved. Color:  ________. 
f.	Background Color:  _____ Front only 
g.	Background Color:  _____ Front and back. 
12.	QR Code Labels: Allow users plugging in luminaires to configure ETC Sensor ThruPower modules to dimmed or switched mode via Wi-Fi connection from ThruPower System Reporter mobile app by ETC Inc.
13.	Standards Compliance: cULus Listed to UL 1573 and CSA C22.2 No. 166.
14.	Power and data distribution equipment to be supplied as shown on project drawings.
2.5	POWERSAFE COMPANY SWITCHES
A.	Product: PowerSafe Company Switch by ETC Inc. A fault-current-limiting option provides additional safety in event of a short circuit, allowing safe connection of equipment with lower Short Circuit Current Rating (SCCR) and reducing arc-flash hazard. 
1.	Model: PSP. PowerSafe Pro: Locking connection covers, shunt-trip protected doors lock connection covers in place while output power is present, and lockout/tagout brackets.
a.	Door-covered "Fingered" cable entry for safe access through front of panel.
b.	Fingered Cable Entry: Foam rubber surface for prevention of wear on cabling.
c.	Double Neutral: Supports 200 percent rated neutral output.
d.	Breaker: 100 percent rated 100 A, 200 A, or 400 A.
e.	LED Worklight: Illuminates interior and output lugs.
2.	Model: PSC. PowerSafe Compact: Does not include connector chamber, dual neutral, tie-off, LED work lights or support for 400 A capacity.
a.	Swing-Hinged Brackets: Lock covers in place until front door is opened, preventing connector insertion under power.
b.	Breaker: 100 percent rated 100 A or 200 A.
3.	Mechanical:
a.	Wall-mount unit with integral keyhole fixing points.
b.	16 ga welded steel cabinet, rated NEMA 1.
c.	Locking swing hinged door with clamp latch.
d.	Fine-textured, scratch-resistant epoxy paint.
e.	Secondary door for access to bare-end tie-ins.
f.	Conduit entry via top or side.
g.	Solid, top, and side panel free of conduit knockouts allow for greater flexibility in contractor conduit entry.
h.	Integral breaker lockout bracket supports standard lockout/tagout procedures to prevent any persons from turning the breaker "on" while the lock is in place.
4.	Electrical:
a.	Power Input: 120/208 V Three-phase, four-wire plus ground.
b.	Copper and aluminum feeders are allowed.
c.	100 percent rated 100 A, 200 A, or 400 A breaker.
d.	65,000A SCCR symmetrical rated system.
e.	Output lugs:
1)	Accommodate up to 4/0 class K cables using 500 kcmil screw terminals.
f.	Single-phase cam-style connector outputs:
1)	Default cam-style connector configuration: 
a)	Phase leg: Female. Ground and Neutral: Male.
2)	Reverse neutral and ground cam-style connector configuration.
a)	Phase leg connectors: Female. Ground and Neutral: Male.
g.	Current Transformers: Can optionally be installed in the field for connection to external third-party power meters.
h.	Shunt trip safety interlock: Disconnects output power when cabinet door is opened.
i.	Short Circuit Current Rating: 65,000 Amp.
j.	Rated Main Breaker: 100 percent.
k.	Iso Ground: Allows isolation between enclosure ground and equipment ground for use with audio systems.
l.	Power Indicators: LEDs light up to show that power is on/available between each phase and neutral.
m.	Lockout/Tagout: Accepts third-party locks on built-in bracket for support of NFPA 70E safety lockout/tagout procedures.
5.	Standards Compliance: cULus. Listed to UL 891 and CSA C22.2 No. 14.
6.	Models and quantities of PowerSafe company switches to be supplied as shown on project drawings.
2.6	EMERGENCY POWER CONTROL PRODUCTS
A.	Product: Automatic Load Control Relay by ETC Inc. A UL924 Listed emergency device that tracks the state of normal power and automatically bypasses control of the load to the emergency state upon loss of the normal power sense feed source. Powered from an always-available normal/emergency source fed by an upstream emergency transfer switch.
1.	Model ALCR-PP-MK2. Automatic Load Control Relay Power Pack.
a.	Mounting:  Uses 1/2 inch (13 mm) knockouts.
2.	Model ALCR-DIN. Automatic Load Control Relay DIN rail mountable.
a.	Mounting:  Uses 1-3/8 inch (35 mm) DIN rail; DIN43880 and EN60715 compliant.
3.	Mechanical:
a.	Constructed of UL94V-0 approved injection-molded ABS.
4.	Electrical:
a.	Power Input: 120/277 VAC, 60 Hz.
b.	Normally closed (NC) relays rated for:
1)	20 A electronic ballasts and driver.
2)	10 A tungsten/ Incandescent.
c.	Terminal wire sizing:
1)	ALCR-PP-MK2: 12 AWG flying leads for power connections, 18 AWG flying leads for sense feed and remote switch.
2)	ALCR-DIN: 10-18 AWG rising clamp terminals.
3)	Remote activation switch can be located up to 1000 ft from ALCR.
5.	Functionality:
a.	Automatic activation of power output to a luminaire or single zone of emergency lighting upon loss of normal power sense feed source.
b.	Supports fire alarm input activation of emergency bypass.
c.	Configurable return to normal delay settings of instant, 10 seconds, 30 seconds, 10 minutes, or 15 minutes.
d.	Low Voltage Control:
1)	Breaks circuit automatically when emergency state activates to drive connected luminaires to emergency levels.
2)	For use with 0-10 V, 1-10 V, DALI, or DMX-controlled luminaires that will automatically send the luminaire to an emergency level upon loss of signal.
3)	Supports use with two-channel 0-10 V luminaires such as tunable white fixtures (ALCR-PP-MK2 only).
e.	Normal delay and bypass test button.
f.	Return-to-normal configuration button.
g.	Two LED indicators:
1)	Status: Red for emergency active, Green for normal active.
2)	Remote: Amber for normal control switch engaged.
6.	Standards Compliance: Listed: UL924.
7.	Models and quantities of Automatic Load Control Relays to be supplied as shown on project drawings.
B.	Product: DMX Emergency Bypass Controller (DEBC) by ETC Inc. A simple cost-effective solution for control bypass of LED house light systems in emergency lighting applications. 
1.	Model DEBC-1 DMX. Emergency Bypass Controller, 1-output.
2.	Model DEBC-6 DMX. Emergency Bypass Controller, 6-output.
3.	Mechanical:
a.	Construction: 18-gauge, formed steel panels.
b.	Finish: Fine-textured powder-coat paint.
c.	Bi-color LED status indicator visible from the exterior of the enclosure.
1)	Green: power is present, and controller is functioning in normal state.
2)	Red: controller is functioning in bypass state.
d.	Recessed test button to manually trigger bypass state is user-accessible without removing covers.
e.	Internally accessible DIP switches for configuration of:
1)	DMX record mode.
2)	Contact input type.
3)	Wait-time to restore incoming DMX (bypass trigger removed).
f.	Internally accessible button for DMX record (snapshot) of bypass preset with an indicator LED for record action.
4.	Electrical:
a.	Supports 100 V to 277 V input power, 50/60 Hz, 0.2 A maximum current draw.
b.	Power input terminals accept two 24- 10 AWG solid or stranded wires.
c.	Grounding lug accepts 14- 2 AWG solid or stranded ground wire.
d.	Bypass contact input supports two 30- 12 AWG low-voltage wires with two modes:
1)	Configurable dry contact input supports maintained normally open (NO) or normally closed (NC) triggering.
2)	Wet contact input for interface with external systems, including fire alarms.
e.	Supports one universe (512 channels) of DMX data compliant with ANSI E1.11- 2008, USITT DMX512-A.
1)	DMX output and DMX input terminals for Belden 9729 cable or equivalent.
f.	Non-volatile memory storage for a single recorded scene of 512 channels.
g.	DEBC-1 passes RDM data in normal mode.
h.	DEBC-6 passes RDM data through DMX Thru port in normal mode.
5.	Thermal:
a.	Ambient room temperature: 32 to 104 degrees F (0 to 40 degrees C).
b.	Ambient humidity: 10- 95 percent non-condensing.
6.	Standards Compliance: Listed: cULus, UL 924, and CSA C22.2 No. 141. CE compliant. RoHS compliant. WEEE compliant.
7.	Models and quantities of DMX Emergency Bypass Controllers to be supplied as shown on project drawings.
C.	Product: Emergency Bypass Detection Kit (EBDK) by ETC Inc. Monitors a single- or three-phase normal power feed and a fire alarm contact and automatically triggers the Panic inputs of connected UL 924 Listed ETC Inc. lighting control products in an emergency.
1.	Mechanical:
a.	Construction: 16 gauge (0.08) steel.
b.	Finish: fine-textured, scratch resistant epoxy paint.
c.	Hinged locking door covers integrated breaker to prevent accidental tripping.
2.	Electrical:
a.	Supports input voltage from 100 V up to 277 V.
b.	Phase loss detection circuitry provides a factory-set delay of 0.5 seconds to prevent nuisance tripping.
c.	Integrated circuit breaker for overcurrent protection and simulation of power loss.
d.	Input and output terminals accept #8 AWG to #22 AWG wiring.
3.	Functionality:
a.	Compatible with single-phase or three-phase lighting systems from 100 V to 277 V.
b.	Provides dry contact closure output to UL 924 ETC Inc. lighting control products for emergency lighting applications.
1)	Includes three output circuits.
2)	Maximum of eight devices wired to each output.
c.	Automatic sensing of normal power loss and fire alarm contact.
d.	Automatically returns to normal lighting operation when normal power is restored, or fire alarm contact is no longer triggered.
4.	Accessories:
a.	Emergency Bypass Detection Kit Restore Switch (EBDK-SWITCH): Manual control station that prevents automatic return to normal lighting look during egress from areas that may be normally dark.
1)	Max of two restore switches per EBDK.
b.	Tap Kits: Provide fuse-protected normal loss sense of mains feeds for ETC Sensor, Sensor IQ, or DRd enclosures.
1)	EBDK-TAP - Unison DRd tap kit.
2)	SR3-TAP - Sensor3 tap kit.
3)	IQ-TAP - Sensor IQ tap kit.
5.	Thermals:
a.	Ambient Room Temperature: 32 to 104 degrees F (0 to 40 degrees C).
b.	Ambient Humidity: 10- 90 percent non-condensing.
6.	Standards Compliance: Listed: cULus and UL 924 emergency lighting and power equipment.
7.	Quantities of Emergency Bypass Detection Kits and related accessories to be supplied as shown on project drawings.
D.	Master Phase Loss Detector 2, Emergency Series by ETC Inc. Extensive, customizable input and output configurations for UL 924 Listed emergency lighting control bypass. 
1.	Model MPLD2. 1/1 MPLD2, 1 Input Card, 1 Output Card.
2.	Model MPLD2. 1/4 MPLD2, 1 Input Card, 4 Output Cards.
3.	Model MPLD2. 2/8 MPLD2, 2 Input Cards, 8 Output Cards.
4.	Model MPLD2. 4/12 MPLD2, 4 Input Cards, 12 Output Cards.
5.	Mechanical:
a.	Construction: 16 ga steel. Hinged Cover for easy access.
b.	Finish: Grey fine-texture powder coat paint.
c.	Mounting: Walls.
d.	Hinged locking door covers integrated breaker to prevent accidental tripping.
6.	Electrical:
a.	Input Voltage: 100 to 277 VAC.
b.	Phase Loss Detection Circuitry: Factory-set delay of 0.5 seconds to prevent nuisance tripping.
c.	Integrated Circuit Breaker: For simulation of power loss.
d.	Input Cards: 
1)	Two dry, normally-closed contact inputs per card. 
e.	Output Cards: 
1)	Four dry, normally-closed contact outputs per card.
2)	Eight devices may be connected to each output.
f.	Wiring Terminations: Made using provided terminals.
g.	Input and Output Terminals: Accept No. 8 AWG to No. 22 AWG wiring.
7.	Thermals:
a.	Ambient Room Temperature: 32 to 104 degrees F (0 to 40 degrees C).
b.	Ambient Humidity: 10 to 90 percent non-condensing.
8.	Accessories:
a.	Emergency Bypass Restore Switch:
1)	Manual control station that prevents automatic return to normal lighting look during egress from areas that may be normally dark.
2)	A single restore switch may be used per MPLD2.
b.	Tap Kits: Provide fuse-protected normal loss sense of mains feeds for ETC Sensor, Sensor IQ, or DRd enclosures.
1)	EBDK-TAP - Unison DRd tap kit.
2)	SR3-TAP - Sensor3 tap kit.
3)	IQ-TAP - Sensor IQ tap kit.
9.	Standards Compliance: Listed: cULus. UL924 Listed as emergency lighting and power equipment. CSA C22.2 No. 141-15, emergency lighting equipment.
10.	Configurations and quantities of Master Phase Loss Detectors to be supplied as shown on project drawings.
E.	Product: SC1008 Branch Circuit ELTS (BCELTS) by ETC Inc. Automatically switches a single 20 A, 120 V or 277 V lighting load from a normal power source to an emergency power source when there is a power failure or other emergency present.
1.	Standards Compliance:
a.	ANSI/UL 1008 Listed Branch Circuit Emergency Lighting Transfer Switch (BCELTS) / Automatic Transfer Switch for use in emergency systems.
1)	Category code WPWR.
2)	UL File E157852.
b.	Complies with Standard CSA C22.2 No. 178 Transfer Switch Equipment.
c.	Complies with ANSI/NFPA 110, Standard for Emergency and Standby Power Systems.
d.	Satisfies Requirements of the National Electric Code (NFPA 70):
1)	Article 700 - Emergency Systems.
2)	Article 701 - Legally Required Standby Systems.
3)	Article 702 - Optional Standby Systems.
4)	Section 518.3C - Assembly Occupancies.
5)	Section 520.8 - Theatres and Similar Locations.
6)	Section 540.11C - Motion Picture Projection Rooms.
2.	NEMA 1 rated steel enclosure. Finish: Fine-textured, scratch resistant epoxy paint.
3.	Mounting: Wall mount with adjustable mounting plate.
4.	Front access to wiring space. Terminal Strips: Clearly marked.
5.	Conduit Entry: Top, bottom, or right side.
6.	Operation:
a.	When Normal Power is Lost with Presence of an Emergency Source: Normal source is disconnected from load and emergency source is connected to load.
b.	When Normal Power is Restored: Emergency source is disconnected from load and normal source is connected to load.
c.	Monitors voltage on normal feed branch circuit.
d.	Emergency State Control Priority:
1)	Power Failure.
2)	Fire Alarm/contact activation.
7.	Electrical:
a.	Normal Feed Input:
1)	Single phase 120- 277 VAC circuit, up to 20 Amps.
2)	Additional terminals provided for constant normal power sense feed when circuit is fed by a dimmer or controlled circuit.
3)	Terminals sized for 10 to 18 AWG wire.
4)	Circuit fed from a remote panel.
b.	Emergency Source Feed Input:
1)	Single phase 120 to 277 VAC circuit, up to 20 A.
2)	Circuit fed from a remote breaker panel supplied by others.
c.	Short Circuit Protection:
1)	Class G Short Circuit Current Rating (SCCR) protection rated for 10,000 Amp RMS symmetrical.
2)	Rated for Continuous Load: 2,400 W per circuit at 120 V. 5,440 W per circuit at 277 V.
3)	Fuse Protection: Allows listed use with any circuit breaker brand.
4)	Current Protection: On load side of contactor. Protects normal and emergency source feeds.
d.	Operation: Switches hot (line) and neutral conductors.
1)	Electrically interlocked to ensure normal power is fully disconnected before emergency power is applied.
2)	Mechanically maintained (held) contactor.
e.	Fire Alarm Input: Field configurable normally closed (NC) or normally open (NO) dry contact input.
1)	Input Terminals: Accept 10 to 20 AWG Class 2 connections from alarm panel.
2)	Ten units can be wired in series to a single contact relay.
3)	Maximum total wire length between contact relay and units is 1,000 ft.
f.	User Controls: Front panel local control includes test button, laser test sensor, and 2 LED status indicators for presence of normal and emergency power.
8.	Relay Ratings:
a.	Magnetic Ballast (HID): 20 Amp.
b.	Electronic Ballast: 16 Amp.
c.	Tungsten: 20 Amp.
d.	Motor at 120 V: 20 Amp (120 Amp Locked rotor).
e.	Motor at 277 V: 14 Amp (84 Amp Locked rotor).
f.	Relays are mechanically held.
g.	Lifespan:
1)	Full Resistive Load: 100,000 cycles.
2)	Motor, Inductive or Tungsten: 30,000 cycles.
9.	Quantities of SC1008 branch circuit transfer switches to be supplied as shown on project drawings.
F.	Product: Emergency Lighting Transfer System, ELTS2 Series by ETC Inc. Switches one or more lighting loads from one power source to another when there is a power failure or other emergency present.
1.	Standards Compliance: Listing: cULus. ANSI/UL 1008 Automatic Transfer Switch for use in emergency systems. Category Code: WPWR. UL File No. E157852.
a.	ANSI/NFPA 110, Standard for Emergency and Standby Power Systems.
b.	Satisfies Requirements of the National Electric Code (NFPA 70):
1)	Article 700 - Emergency Systems.
2)	Article 701 - Legally Required Standby Systems.
3)	Article 702 - Optional Standby Systems.
4)	Section 518.3C - Assembly Occupancies.
5)	Section 520.8 - Theatres and Similar Locations.
6)	Section 540.11C - Motion Picture Projection Rooms.
c.	Self-contained system for up to 24 circuits.
d.	Short Circuit Current Rating (SCCR): 65,000 Amp RMS symmetrical at 277 VAC.
e.	Standard enclosure is NEMA 1; optional enclosure is NEMA 4.
f.	Seismic Certification: Independent lab certification and third-party testing complies with the US seismic requirements of the International Building Code (IBC) for equipment in the emergency life-safety chain.
1)	IBC 2000 - referencing ASCE 7-98 and ICC AC-156.
2)	IBC 2003 - referencing ASCE 7-02 and ICC AC-156.
3)	IBC 2006 - referencing ASCE 7-05 and ICC AC-156.
4)	IBC 2009 - referencing ASCE 7-05 and ICC AC-156.
2.	Mounting: Wall unit. Vertical.
3.	Mounting: Wall unit. Horizontal.
4.	Construction: 14 ga welded steel cabinet. NEMA 1 or NEMA 4 rating.
5.	One-point, small unit or three-point, large unit door latch with key lock.
6.	Finish: Fine-textured scratch resistant epoxy paint
7.	Hinged front access to wiring space for contractor connections. 
a.	Clearly marked termination strips and phase voltage lugs.
8.	Conduit entry via top, bottom, or from any side.
9.	Control Wiring: Separated from higher voltage wires to avoid contact during installation.
10.	Operation: Monitors normal power, and upon detection of power failure with presence of an emergency source, the ELTS2 disconnects normal source and connects emergency source.
a.	When Normal Power is Restored: Emergency source is disconnected from the loads and normal source is connected to the loads.
b.	Monitors voltage on all normal phases.
c.	Field-adjustable delay after a loss of normal power before switching to the emergency source; adjustable from 0 to 10 seconds.
d.	Field-adjustable delay after the restoration of normal power before switching to normal source; adjustable from 0 to 60 seconds.
e.	Emergency State Control Priority:
1)	Power fail.
2)	Fire alarm activation.
3)	Local and/or remote activation.
11.	Electrical:
a.	Normal Sense Circuit Input: AC circuits with neutral to provide power to the normal side of the electronics and for sensing a power fail.
1)	Power:  120 V Discrete Feed - Three phase, 4 wire.
2)	Power:  277 V Discrete Feed - Three phase, 4 wire.
3)	Power:  120/208 V Main Feed - Three phase, 4 wire.
4)	Power:  120/240 V Main Feed - Single phase, 3 wire.
5)	Power:  230/400 V Main Feed - Three phase, 4 wire.
6)	Power:  277/480 V Main Feed - Three phase, 4 wire.
7)	Terminals sized for 8 AWG wire.
8)	Separate units required for mixed voltages.
b.	Emergency Source Feed:
1)	Type D: Each circuit discretely fed from a remote breaker panel.
a)	Configuration:  20 Amp, 120 V circuits.
b)	Configuration:  20 Amp, 230 and 240 V circuits.
c)	Configuration:  20 Amp, 277 V circuits.
2)	Type M: Single feed main lugs distribute emergency power to all circuits.
a)	Configuration:  120/208 V - Three phase, 4 wire.
1)	80 A for 12 circuits / 160 Amps for 24 circuits. 
b)	Configuration:  120/240 V - Single phase, 3 wire.
1)	120 Amps for 12 circuits / 240 Amps for 24 Circuits. 
c)	Configuration:  230/400 V - Three phase, 4 wire.
1)	80 A for 12 circuits / 160 Amps for 24 circuits. 
d)	Input Lug Wire Range:
1)	Small:  14 AWG - 2/0 for 12 circuits. 
2)	Large:  6 AWG - 350 kcmil for 24 circuits. 
3)	Fuse Protection: Allow listed use with any circuit breaker brand.
a)	Class G SCCR protection.
b)	Located on load side of contactor. Protects both normal and emergency source feeds.
c.	Maximum Continuous Load Contactors:
1)	20 Amp circuits rated for continuous load of 1920 W per circuit at 120 V, 3680 W per circuit at 230 V, and 4432 W per circuit at 277 V.
2)	A single contactor set controls no more than 2 circuits.
3)	Switches hot and neutral conductors.
4)	Mechanically interlocked to ensure a break before make.
5)	Rated for Mixed Loads: Resistive, tungsten and discharge lamps.
6)	Mechanically maintained.
d.	Fire Alarm Input: Normally closed dry contact closure.
1)	Input terminals accept 10 to 22 AWG class 2, two-wire from alarm panel.
12.	User Controls: Front panel local control includes a test key switch and 3 indicators.
a.	Test key switch: Three-position momentary key switch.
1)	Normal Mode with indicator.
2)	Emergency Mode with indicator.
3)	Fire Alarm with indicator.
b.	Allows connection of five remote control stations; 5-wire, 24 V Class 2, tested 16 AWG up to 1,000 ft.
13.	Configurations and quantities of ELTS2 transfer switches to be supplied as shown on project drawings.
PART 3    EXECUTION
3.1	EXAMINATION
A.	Do not begin installation until substrates have been properly constructed and prepared.
B.	If substrate preparation is the responsibility of another installer, notify Architect in writing of unsatisfactory preparation before proceeding.
3.2	PREPARATION
A.	Clean surfaces thoroughly prior to installation.
B.	Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.
3.3	INSTALLATION
A.	Install in accordance with manufacturer's instructions, approved submittals, and in proper relationship with adjacent construction.
3.4	FIELD QUALITY CONTROL
A.	Field Inspection: Coordinate field inspection in accordance with appropriate sections in Division 01.
B.	Manufacturer's Services: Coordinate manufacturer's services in accordance with appropriate sections in Division 01.
3.5	CLEANING AND PROTECTION
A.	Clean products in accordance with the manufacturers recommendations. 
B.	Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION